## Input
SLIMDUCT RD Size Calculator
Insulation Wall Thickness | [8 empty] | 0
0
0
Pipe Size | Liquid | Suction | Suction 2 | Number of system |  |  |  |  | 0
System 1 |  |  |  |  | 12.7x12.7 |  | 1/2x1/2 |  | 0
System 2 |  |  |  |  | 19.05x19.05 | 6.35 | 3/4x3/4 | 1/4 | 0
System 3 |  |  |  |  | 25.4x25.4 | 9.52 | 1x1 | 3/8 | 0
System 4 |  |  |  |  | 10x10 | 12.7 | 13/32x13/32 | 1/2 | 0
System 5 |  |  |  |  | 10x20 | 15.88 | 13/32x25/32 | 5/8 | 0
System 6 |  |  |  |  | 20x20 | 19.05 | 25/32x25/32 | 3/4
System 7 | [5 empty] | 22.22 |  | 7/8
System 8 | [5 empty] | 25.4 |  | 1
System 9 | [5 empty] | 28.58 |  | 1-1/8
System 10 | [5 empty] | 31.75 |  | 1-1/4
System 11 | [5 empty] | 34.92 |  | 1-3/8
System 12 | [5 empty] | 38.1 |  | 1-1/2
System 13 | [5 empty] | 41.28 |  | 1-5/8
System 14 | [5 empty] | 44.45 |  | 1-3/4
System 15 | [5 empty] | 50.8 |  | 2
System 16 | [5 empty] | 53.98 |  | 2-1/8
System 17
System 18
System 19
System 20
Select the pipe size from the options provided below.
'Number of system' needs to be input manually.
Confirm
Please press confirm to calculate the recommended duct size.
Select the insulation thickness from the options provided below. (Liquid×Suction)
Note : The wall thickness is described in inch. For metric, 13/32 and 25/32 is equivalent to 10mm and 20mm.

## Outcome (hidden)
SLIMDUCT RD Size Calculator Outcome
Duct Size | Availability | Ratio of Occupancy |  |  | 有効寸法 | 有効寸法 | 断面積（㎟） | 配管総断面積 （㎟）
[5 empty] | 幅（mm） | 高さ（mm）
RD-150 | Not Available | 102% |  |  | 150 | 97 | 14550 | 14709.3301
RD-300 | Available | 53% |  |  | 300 | 93 | 27900 | 14709.3301
RD-300H | Available | 24% |  |  | 300 | 213 | 63900 | 14709.3301
RD-450 | Available | 36% |  |  | 450 | 93 | 41850 | 14709.3301
RD-450H | Available | 16% |  |  | 450 | 213 | 95850 | 14709.3301
RD-600 | Available | 27% |  |  | 600 | 93 | 55800 | 14709.3301
RD-600H | Available | 12% |  |  | 600 | 213 | 127800 | 14709.3301
RD-900 | Available | 18% |  |  | 900 | 93 | 83700 | 14709.3301
RD-900H | Available | 8% |  |  | 900 | 206 | 185400 | 14709.3301
Pipe Description
Insulation Wall Thickness | 13/32x25/32
Pipe Size | Liquid | Suction | Suction 2 | Number of System
System 1 | 3/8 | 1/2 | 3/8 | 3
System 2
System 3
System 4
System 5
System 6
System 7
System 8
System 9
System 10
System 11
System 12
System 13
System 14
System 15
System 16
System 17
System 18
System 19
System 20
Back
Print
To be safe, 70% occupancy will be the border line of the judgement.
More or less pipe could be enclosed depending on the actual situation.
This outcome is based on calculation and won't be guaranteed.
The result may differ depending on the actual situation.

## list (hidden)
配管径（mm） | 実際の保温材厚（mm） | ソフト上保温材厚（mm） | 外径（mm） | 断面積（㎟）
6.35 | 8 | 10 | 24 | 452.16
| 20 | 20 | 48 | 1808.64
| 12.7 | 12.7 | 33 | 854.865
| 19.05 | 19.05 | 45 | 1589.625
| 25.4 | 25.4 | 58 | 2640.74
9.52 | 8 | 10 | 27 | 572.265
| 20 | 20 | 51 | 2041.785
| 12.7 | 12.7 | 36 | 1017.36
| 19.05 | 19.05 | 49 | 1884.785
| 25.4 | 25.4 | 61 | 2920.985
12.7 | 10 | 10 | 34 | 907.46
| 20 | 20 | 54 | 2289.06
| 12.7 | 12.7 | 39 | 1193.985
| 19.05 | 19.05 | 52 | 2122.64
| 25.4 | 25.4 | 65 | 3316.625
15.88 | 10 | 10 | 37 | 1074.665
| 20 | 20 | 57 | 2550.465
| 12.7 | 12.7 | 42 | 1384.74
| 19.05 | 19.05 | 55 | 2374.625
| 25.4 | 25.4 | 68 | 3629.84
19.05 | 10 | 10 | 41 | 1319.585
| 20 | 20 | 61 | 2920.985
| 12.7 | 12.7 | 46 | 1661.06
| 19.05 | 19.05 | 58 | 2640.74
| 25.4 | 25.4 | 71 | 3957.185
22.22 | 10 | 10 | 44 | 1519.76
| 20 | 20 | 64 | 3215.36
| 12.7 | 12.7 | 49 | 1884.785
| 19.05 | 19.05 | 61 | 2920.985
| 25.4 | 25.4 | 74 | 4298.66
25.4 | 10 | 10 | 47 | 1734.065
| 20 | 20 | 67 | 3523.865
| 12.7 | 12.7 | 52 | 2122.64
| 19.05 | 19.05 | 65 | 3316.625
| 25.4 | 25.4 | 77 | 4654.265
28.58 | 10 | 10 | 50 | 1962.5
| 20 | 20 | 70 | 3846.5
| 12.7 | 12.7 | 55 | 2374.625
| 19.05 | 19.05 | 68 | 3629.84
| 25.4 | 25.4 | 80 | 5024
31.75 | 10 | 10 | 53 | 2205.065
| 20 | 20 | 73 | 4183.265
| 12.7 | 12.7 | 58 | 2640.74
| 19.05 | 19.05 | 71 | 3957.185
| 25.4 | 25.4 | 84 | 5538.96
34.92 | 10 | 10 | 57 | 2550.465
| 20 | 20 | 76 | 4534.16
| 12.7 | 12.7 | 61 | 2920.985
| 19.05 | 19.05 | 74 | 4298.66
| 25.4 | 25.4 | 87 | 5941.665
38.1 | 10 | 10 | 60 | 2826
| 20 | 20 | 80 | 5024
| 12.7 | 12.7 | 65 | 3316.625
| 19.05 | 19.05 | 77 | 4654.265
| 25.4 | 25.4 | 90 | 6358.5
41.28 | 10 | 10 | 64 | 3215.36
| 20 | 20 | 84 | 5538.96
| 12.7 | 12.7 | 68 | 3629.84
| 19.05 | 19.05 | 80 | 5024
| 25.4 | 25.4 | 93 | 6789.465
44.45 | 10 | 10 | 66 | 3419.46
| 20 | 20 | 86 | 5805.86
| 12.7 | 12.7 | 71 | 3957.185
| 19.05 | 19.05 | 84 | 5538.96
| 25.4 | 25.4 | 96 | 7234.56
50.8 | 15 | 10 | 83 | 5407.865
| 20 | 20 | 93 | 6789.465
| 12.7 | 12.7 | 77 | 4654.265
| 19.05 | 19.05 | 90 | 6358.5
| 25.4 | 25.4 | 103 | 8328.065
53.98 | 15 | 10 | 86 | 5805.86
| 20 | 20 | 96 | 7234.56
| 12.7 | 12.7 | 80 | 5024
| 19.05 | 19.05 | 93 | 6789.465
| 25.4 | 25.4 | 106 | 8820.26